INSTIUTE OF MICROBIAL TECHNOLOGY

(COUNCIL OF SCIENTIFIC & INDUSTRIAL RESEARCH)

SECTOR-39-A, CHANDIGARH

Subject:	Tender for annual Non-Comprehensive Maintenance/Repairs/ Round-the-clock, operation & testing of fire fighting system at IMTECH, Sector 39A, Chandigarh

CONTENTS

| Sr.No. | Description | Page No. |
| --- | --- | --- |
| 1 | NIT | 1 |
| 2. | Terms & Conditions (Annexure-I) | 2-8 |
| 3. | Description of work (Annexure-II) | 9 |
| 4. | Proforma to be filled by contractor (Annexure-III) | 10 |

Note:	Tenderer should confirm that they have received all the above papers from Sr.2 to and seen and understood all items.  All the documents are to be returned duly signed by the tenderer who has submitted his offer.

TENDER ISSUED TO

M/S__________________________

_____________________________

_____________________________

Tel.No., if any_________________________

Signature of Officer issuing tender

Pay Order/Demand Draft No._____________ dated _______________ from the Bank ______________________________________________________ drawn in favour of Director, IMTECH, Chanidgarh for Rs.___________ (Rupees_____________________________________) is enclosed herewith.

---------------------------------------------------------------------------------------------------

I/We have read and understood all the terms and conditions and all other relevant documents and seen the drawings if any and visited the site before quoting the rates.

Signature of the Contractor

Address____________________

___________________________

___________________________

Telephone/Mobile No.____________________

INSTITUTE OF MICROBIAL TECHNOLOGY

(Council of Scientific and Industrial Research)

SECTOR-39-A, CHANDIGARH

Advt No.2(358)/2011-Gen

NOTICE INVITING TENDER

Sealed quotations for Annual non-comprehensive round the clock maintenance, repair operation and testing of fire fighting and detection system including sprinkler, motors, pump, engine, hose pipe, stand post, hydrants, NRV sluice valve, fire and smoke detector, conduit floor pipes and panel or RINCP alarm system, talk back public address system and distribution of water supply lines and risers, electrical panels etc. at IMTECH for a period of one year are invited from the eligible firms, holding following & is required to produce attested copies thereof:

i) Valid licence under Contract Labour (Regulation Abolition) Act 1970.

ii) Registered with EPFO, ESIC, having Service tax registration, having labour licence,  latest I.T.Certificate, Solvency Certificate etc..H

iii) Having registration with Police authorities.

iv) Status: whether proprietor/firm/company.

Detailed tender documents can be obtained against a written request quoting Advt No. accompanied by a crossed demand draft or in cash for Rs.500.00 (Rupees five hundred only) (non-refundable) from any scheduled bank drawn in favour of Director, IMTECH payable at Chandigarh.

i)	Sale of tender document 			          :10.10.2011 to 27.10.2011

ii)	Cost of tender document 				:Rs.500/-(non-refundable)

iii)	Last date and time for submission of tender	:28.10.2011 upto 1500 Hrs.

iv)	Date and time of tender/quotation opening :28.10.2011 upto 1530 Hrs.

v)	Earnest money Deposit (EMD) to be submitted alongwith 	quotation/tender:	Rs.20, 000/- (Rupees Twenty Thousand only)

vi)     Offer by Fax / E-mail will be summarily ignored.

This advertisement and detailed tender document are also available on IMTECH website “www.imtech.res.in”. If the tender document is downloaded from the website, please enclose the cost of the tender document in the form of Demand draft. Incomplete tender or tenders received without EMD shall be summarily rejected.

The Director, IMTECH reserves the right to accept/reject any or all the tenders without assigning any reason.

Administrative Officer

ANNEXURE-I

Subject:	Tender for annual Non-Comprehensive Maintenance/Repairs/ Round-the-clock, operation & testing of fire fighting system at IMTECH, Sector 39A, Chandigarh

Approximate Amount: Rs.2,77,000/- (Rupees Two Lakh  Seventy Seven Thousand only)

The Director, IMTECH, invites quotations for:

1.	Annual non-comprehensive round the clock maintenance, repair operation and testing of fire fighting and detection system including sprinkler, motors, pump, engine, hose pipe, stand post, hydrants, NRV sluice valve, fire and smoke detector, conduit floor pipes and panel or RINCP alarm system, talk back public address system and distribution of water supply lines and risers, electrical panels etc. at IMTECH for a period of one year as per details attached. The contractor may quote lump-sum rate including taxes, if any.

TERMS & CONDITIONS:

- This contract covers annual maintenance, repairs, operation and testing of fire fighting and detection including sprinkler motors, engine hose pipes, stand posts, hydrants, NRV, S.V. fire and smoke detectors, conduit floor panels RINCP alarm system talk back public address system distribution water supply lines and risers etc. complete

- Contractor shall deploy competent service Engineer/Technical persons to operate /keep the system functional round the clock.

- The firm will ensure that control system is manned round the clock by his competent staff to ensure timely action in case of any mishappening in building.

- The work shall be carried out as per direction and as per the satisfaction of IMTECH Nodal Officer.

- The system maintained in the schedule shall be kept in good working condition by the firm during contract period as per detailed below:

  - Cleaning and maintaining control system including all equipment installed therein. Logbooks should be maintained and signed by the Imtech nodal officer.

  - Servicing, performance check and repair as and when required of all the equipments i.e., sprinkler, motors, engine hose pipe, stand post, hydrants, NRV, S.V. fire detectors (smoke and fire), conduit wire, panels, response indicators, manual call point alarm system, talk back public address system, riser, water tank etc.

  - Cost for round the clock annual maintenance, repairs and operations of all the systems are included in the rates.

Contd….p/2…..

-: 2 : -

- The material for any defect arising in the fire fighting system shall be arranged by the AMC contractor as per the rate contract made at the time of award of contract. The AMC contractor will carry out rectification of such defect within three days of being intimated failing which a penalty of Rs 200/- per day shall be imposed on the contractor.

- All T & P  ( Tools & Plants),  cleaning or any other material, consumables etc required  to execute the work for rectification of any defect arising in the fire fighting system/ routine maintenance  shall be arranged by the AMC contractor free of cost on his own.

- No extra charges would be payable with regard to the labour deployed by the AMC contractor for rectification of any defect arising in the fire fighting system as the same is included in the charges being paid for the AMC contract.

Scope of Contractors responsibility

MANPOWER

- The contractor shall deploy minimum one qualified fire safety staff round the clock in each shift. They shall have the following qualifications:-

ITI in mechanical/ electrical engineering with at least 1 year experience of maintenance of fire fighting systems and fire fighting.  It would be their duty to keep all the fire fighting/detection equipment etc. in an operational state at all times and to carry out fire fighting as per laid down fire safety procedures in case of a fire.

- Nodal Officer will be at liberty to turn out any of the contractors staff if found in undesirable activities and no worker will be allowed to reside at the place of duty.

- The contractor shall arrange all required tools and manpower for attending testing/checking/servicing of installed equipment.

Contd….p/3…..

-: 3 : -

- Cost for round the clock annual maintenance, repairs and operations of all the system round the clock are included in the rates.

- Logbook and stationery as required shall be maintained by the contractor for fire alarm and PA system so that complete system can be checked by the department.

- The contractor shall not dismantle any item without the knowledge of IMTECH authorized officer.

- In case of any loss of life/injuries to manpower deployed by the contractor shall be the sole responsibility of the contractor.

- Any loss to the life and property due to negligence/non-functioning of the system shall be the responsibility of the contractor.

FIRE FIGHTING

PART- I (SCOPE OF MAINTENANCE )

- To maintain the system in clean & healthy working condition.

- Carry out drills/tests/maintenance routine as specified in part III.

- Operate Fire Fighting system when required.

- The vendor shall arrange, at his costs, inspection by authorized Engine service station and shall submit its health check report to IMTECH twice in a year (April and October)

PART – II ( TASKS TO BE PERFORMED WITHIN 15 DAYS)

- Contractor shall Identify person(s) for fire fighting system maintenance and operation as per prescribed qualification & experience. Familiarize them with the system and its working and ensure that they will be able to operate it when required.

- Inspect the entire installation for proper working, shortcomings to be recorded and brought to the notice of Nodal Officer.

- Educate maintenance Personnel, regarding steps to be taken in case of fire.

PART- III ( MAINTENANCE SCHEDULE TO BE FOLLOWED).

- Test the working of wet-riser system including Diesel pump & alarms every day. The procedure to be decided in consultation with IMTECH Nodal officer and recorded for future reference.

Contd….p/4…..

-: 4 : -

- Organize a drill once in a month to demonstrate proper functioning of the system in consultation with IMTECH Nodal officer. Record of such exercise to be kept duly signed by  IMTECH Nodal officer.

- Daily check of the water pressure in the system, minimum pressure 3.5kgs/cm2 at the farthest point of the building.

- Daily check of the water in the Fire fighting underground Tank, If water not available necessary arrangements to be made.

- Oil change, filter change of diesel engine shall be done as per manufacturer’s recommendation.

- Painting of yard hydrants, cabinets, air vessels, exposed pipes once a year during the month of April.

PART IV (MATERIALS)

The material required shall be arranged by the AMC contractor as per rate contract made at the time of award of contract.

PART V (SPECIAL CONDITIONS RELEVANT TO PARTICULAR JOB/PARTICULAR SITE)

- In case of fire the maintenance staff of the AMC firm shall organize First Aid operations.

- He will also inform facility in-charge/fire brigade/Security Supervisor/Security Officer immediately.

- Arrange inspection by expert if desired by engineer-in-charge to identify persistent problem.

- Failure of system during fire will invite action as deemed fit by Director, IMTECH.

- Unsatisfactory working of system during monthly drills shall also invite penalty of Rs 500/ per incident.

FIRE DETECTION.

PART I (SCOPE OF MAINTENACE)

- To ensure that complete fire detection system is always clean and in healthy working condition.

- Perform daily checks as per part-III

- To perform tasks subsequent to a real alarm situation as per part-III.

- Keep Fire extinguishers in working condition including recharging once in an year or earlier if required. The recharging shall be arranged in 3 to 4 lots.

Contd….p/5…..

-: 5 : -

- Ensure that adequate quantity of sand is always available in fire buckets.

- Ensure 06 monthly testing of smoke/heat detectors, manual call points, alarm panels etc.

PART –II ( TASKS TO BE PERFORMED WITHIN 15 DAYS)

- Familiarize the maintenance personnel with the Fire detection and alarm system and their responsibility in consultation with IMTECH Nodal officer.

- Inspect the complete system for proper functioning. Any shortcoming noticed should be recorded and brought to the notice of IMTECH Nodal officer .

- Finalize detector cleaning and Zone testing schedule (refer Section III below).

- Ensure that maintenance staff can operate Fire extinguishers/ Fire pumps.

- Educate maintenance personnel regarding steps to be taken in case of fire.

PART- III (MAINTENANCE SCHEDULE TO BE FOLLOWED)

- Check working of PA system on daily basis.

- Check working of F/D system from the control panel on daily basis.

- Detectors to be cleaned during April and October months from the outside and once a year (October) with blower. During this activity the system should remain in working condition.

- The contractor shall replace the set of batteries once during the currency of contract.

NOTE:-

- The methodology to be worked out in consultation with Engineer-in charge/ nodal officer as the same may very according to number of detectors/zones.

- The firm has to demonstrate (Fire Drill) to IMTECH Nodal officer, proper working of the entire fire detection system including PA system once a month. Deficiencies, if any, noticed during demonstration shall be attended within a week’s time. The result of fire drill shall be submitted along with the monthly bill.

- In case of fire alarm it is expected that the maintenance person has to immediately rush to the trouble spot and also inform security supervisor/facility in-charge/fire department. He should also take “First aid” steps depending upon situation. Specific details for first aid steps to be worked out in consultation with IMTECH Nodal officer and kept on record.

Contd….p/6…..

- : 6 : -

- In case of persistent problem or if required by the Engineer-in-charge/ IMTECH Nodal officer arrange an inspection by an expert in the fire detection system for identifying defects and solutions.

PART-IV(MATERIALS)

The material required shall be arranged by the AMC contractor as per rate contract made at the time of award of contract.

PART V (SPECIAL CONDITIONS RELEVANT TO PARTICULAR JOB/PARTICULAR SITE)

- Any addition/alteration during the period of contract shall be maintained by the firm and nothing extra shall be payable on this account.

- Failure of system to activate in the event of smoke/fire will invite action as deemed fit by Director, IMTECH.

MISC. CONDITIONS:

- Water and electricity will be provided free of cost to the contractor for   the maintenance and operation of the system.

- Contractor shall be abiding by the security arrangement/regulation of the building and other regulations in force.

- Temporary passes and uniform will be issued by the contractor to its personnel.

- Any material taken out from the building shall have necessary permission from the competent authority in the form of gate pass.

- The contractor shall quote the rates of items including taxes etc. as  given in the detail work which may be required time to time for repairs/maintenance. Only standard approved makes may be quoted along with quotations.

- The contractor shall be responsible for his employee welfare statutory requirements as per rules, any labor or staff related problem/disputes will be the sole responsibility of the contractor and IMTECH will not be responsible in any way of the payment on the account of such problem/disputes. All the labor laws shall be complied by the contractor and IMTECH will not be responsible in any way of the payment of the account.

Contd….p/7…..

-: 7 : -

- Any contract person found incompetent/unsuitable or misbehaving or not complying with the instructions shall be replaced immediately under the instruction of the IMTECH authorized officer.

Liability of the contractor to indemnify:

The contractor shall keep the IMTECH indemnified against any loss caused to the IMTECH’s property by way of theft, mishandling or otherwise and the claims whatsoever in respect of the employees deployed by the contractor.  Contractor shall be responsible for payment of any loss caused to the property of the IMTECH. In case any employee of the contractor so deployed enters into dispute of any nature whatsoever, it will be the sole responsibility of the contractor concerned to contest the same. In case the IMTECH is also to implead as a party, the cost, if any of the actual expenses incurred towards counsel fee and other expenses shall be paid to the IMTECH by the contractor in advance or on demand. Further, the contractor shall ensure that no financial or any other legal liability comes on the IMTECH in this respect at any time for the acts done by the personnel of the contractor.

Terms of Payment:

  - The payment shall be made proportionally on monthly basis within one week of submission of bill after rendering satisfactory services and duly certified by the IMTECH nodal officer.

  - All taxes are included in the lump sum rates.

  - Work satisfaction report from authorized officer shall accompany the bill

- All other terms and conditions shall be as per agreement and approved by Director, IMTECH.

10.    The Director Imtech has right to terminate the contract by giving one month notice without citing any reason

Annexure-II

PROVIDING NON-COMPREHENSIVE AMC OF COMPLETE FIRE FIGHTING SYSTEM AND ROUND THE CLOCK OPERATION AT IMTECH. BUILDING SECTOR 39-A, CHANDIGARH.   FOR A PERIOD ONE YEAR.

| S. No. | Description of Work |  |
| --- | --- | --- |
| 1 | Providing non-comprehensive AMC and round the clock operations. and servicing of complete automatic fire detection and fire alarm system and P.A system installed in IMTECH building sec.39 Chandigarh . The system shall be tested Tiime to time and serviced once in a month and the report of complete in every month. the job includes the testing and servicing of all equipments as per details given below:- - Main control panel 16 zone =1 No - Main control mimic panel 16 zone - Sub Main Control panel 8 zone - Main mimic panel 8 zone - Fire alarm panel 8 zone - Two way talk back system - 8 zone monitor panel = - Two way talk back system - 12V Batteries - Local control panel 2 zone. - Smoke detectors . - Optical smoke detectors - Heat detectors - Response Indicator. - Manual break glass push button - Hooters - RMS Amplifier - Microphone - Speaker 20 W - Speaker 4 W - Main electric motor pump - Jockey Pump - Diesel engine pump - Main electrical panel - Diesel engine charger & panel - Hose Pipe of hydrants and wetrisers - Hose reel drum with rubber pipe - Air visals - External water filling points for fire vechile - Yard hydrants - Landing valve - S.Valve - pipes (over or U/G) - ABC type fire extinguishers - CO2 type fire extinguishers - DCP type fire extinguishers - foam type fire extinguishers |  |

Annexure-III

INSTITUTE OF MICROBIAL TECHNOLOGY,

SECTOR 39 A, CHANDIGARH

Rates for annual Non-Comprehensive Round the clock  maintenance, repair, operation & testing of fire fighting system  as per our Tender Documents :-

(Rs. __________________________ )

(Rupees ____________________________________________________)

Proportionate Rates ( Monthly)	Rs. ___________________ per month

Signature of the Contractor

with SEAL

INSTITUTE OF MICROBIAL TECHNOLOGY

SECTOR-39-A, CHANDIGARH

INVITING TENDERS

No.IMTECH- No.2(358)/2011-Gen.

Sealed quotations for Annual non-comprehensive round the clock maintenance, repair operation and testing of fire fighting and detection system including sprinkler, motors, pump, engine, hose pipe, stand post, hydrants, NRV sluice valve, fire and smoke detector, conduit floor pipes and panel or RINCP alarm system, talk back public address system and distribution of water supply lines and risers, electrical panels etc. at IMTECH for a period of one year are invited from the eligible firms.

The full details of advertisement of NIT are available on IMTECH website “www.imtech.res.in”.

Administrative Officer